## technologies and projects
financial base year |  | 1987 O&M inflator | 2011 inflator | 2007 inflator | 2018 inflator
2016 |  | 1.8601 | 1.0787 | 1.1443 | 0.95964
| Data from HSIS Appendix A, http://www.hnei.hawaii.edu/sites/www.hnei.hawaii.edu/files/Hawaii%20Solar%20Integration%20Study%20-%20Oahu.pdf | [7 empty] | min->2 | 2->3 | 3->4 | 4->max
[5 empty] | Power Points (MW) |  |  |  |  | Incremental Heat Rate (Btu/kWh) |  |  |  |  | Variable Cost |  | Outages | Fuel Consumption (MMBTU/hour)
[5 empty] | PP | PP | PP | PP | PP | IHR | IHR | IHR | IHR |  |  |  |  | FC | FC | FC | FC | FC
| technology | Plant | Fuel | Fuel Input @ Min Power (MMBtu) | Min | 2 | 3 | 4 | Max | 1 | 2 | 3 | 4 | Full Load Heat Rate (Btu/kWh) | Variable O&M ($/mwH) | Variable Cost ($/Hour) | FOR % | Min | 2 | 3 | 4 | Max | Full load heat rate (calculated) | Err vs inc curve | 2018 full load heat rate | err vs. reported
| Honolulu_8 | H8 | LSFO | 268.4 | 22.3 | 30.1 | 37.9 | 45.6 | 53.4 | 10579 | 10667 | 10755 | 10843 | 11265 | 0.32 |  | 15.1% | 268.4 | 350.9162 | 434.1188 | 516.9323 | 601.5077 | 11.2642 | -0.00081086
| Honolulu_9 | H9 | LSFO | 279.6 | 22.3 | 30.3 | 38.4 | 46.4 | 54.4 | 10080 | 10433 | 10785 | 11138 | 11400 | 0.32 |  | 15.1% | 279.6 | 360.24 | 444.7473 | 531.0273 | 620.1313 | 11.3995 | -0.00052757
| Waiau_3 | W3 | LSFO | 295.5 | 22.3 | 28.4 | 34.5 | 40.5 | 46.6 | 9115 | 10150 | 11185 | 12220 | 11904 | 0.32 |  | 15% | 295.5 | 351.1015 | 413.0165 | 480.1265 | 554.6685 | 11.9028 | -0.0012425 | 11.0085 | -0.89424
| Waiau_4 | W4 | LSFO | 272.3 | 22.3 | 28.4 | 34.5 | 40.5 | 46.6 | 10904 | 11292 | 11680 | 12068 | 11832 | 0.32 |  | 12% | 272.3 | 338.8144 | 407.6956 | 477.7756 | 551.3904 | 11.8324 | 0.00041202 | 11.0085 | -0.8239
| Waiau_5 | W5 | LSFO | 273.7 | 22.5 | 30.5 | 38.5 | 46.5 | 54.5 | 10364 | 10840 | 11316 | 11791 | 11526 | 0.32 |  | 4.7% | 273.7 | 356.612 | 443.332 | 533.86 | 628.188 | 11.5264 | 0.00038532 | 11.0085 | -0.51787
| Waiau_6 | W6 | LSFO | 276.2 | 22.5 | 30.3 | 38 | 45.8 | 53.5 | 10399 | 10893 | 11388 | 11882 | 11618 | 0.32 |  | 4.7% | 276.2 | 357.3122 | 441.1883 | 530.0147 | 621.5061 | 11.6169 | -0.0010636 | 11.0085 | -0.60842
| Waiau_7 | W7 | LSFO | 316 | 27 | 41 | 55 | 68.9 | 82.9 | 9247 | 9794 | 10340 | 10887 | 10600 | 0.32 |  | 5.2% | 316 | 445.458 | 582.574 | 726.3 | 878.718 | 10.5997 | -0.00026538 | 11.0085 | 0.40878
| Waiau_8 | W8 | LSFO | 314.1 | 27 | 41.8 | 56.6 | 71.3 | 86.1 | 8971 | 9358 | 9746 | 10133 | 10204 | 0.32 |  | 5.2% | 314.1 | 446.8708 | 585.3692 | 728.6354 | 878.6038 | 10.2045 | 0.00045761 | 11.0085 | 0.80406
| Waiau_9 | W9 | Diesel | 245.3 | 5.9 | 17.7 | 29.4 | 41.2 | 52.9 | 8514 | 9199 | 9883 | 10568 | 13115 | 3.3738 | 99.19 | 10.9% | 245.3 | 345.7652 | 453.3935 | 570.0129 | 693.6585 | 13.1126 | -0.0023629 | 25.3958 | 12.2832
| Waiau_10 | W10 | Diesel | 234.7 | 5.9 | 16.9 | 27.9 | 38.9 | 49.9 | 7904 | 8529 | 9155 | 9780 | 12499 | 3.5552 | 99.19 | 10.9% | 234.7 | 321.644 | 415.463 | 516.168 | 623.748 | 12.5 | 0.00095992 | 25.3958 | 12.8958
| Kahe_1 | K1 | LSFO | 387.9 | 36.5 | 47.9 | 59.3 | 70.7 | 82.1 | 9237 | 9531 | 9825 | 10118 | 10101 | 0.32 |  | 3.6% | 387.9 | 493.2018 | 601.8552 | 713.8602 | 829.2054 | 10.0999 | -0.001056 | 10.6678 | 0.56783
| Kahe_2 | K2 | LSFO | 383.4 | 36.7 | 48.1 | 59.4 | 70.8 | 82.1 | 9365 | 9444 | 9524 | 9603 | 9915 | 0.32 |  | 3.6% | 383.4 | 490.161 | 596.8782 | 705.4518 | 813.9657 | 9.9143 | -0.00067966 | 10.6678 | 0.75346
| Kahe_3 | K3 | LSFO | 373.9 | 36.3 | 48.8 | 61.2 | 73.7 | 86.1 | 9030 | 9188 | 9345 | 9502 | 9703 | 0.32 |  | 5.2% | 373.9 | 486.775 | 600.7062 | 717.5187 | 835.3435 | 9.702 | -0.0009849 | 10.6678 | 0.96576
| Kahe_4 | K4 | LSFO | 390.5 | 36.3 | 48.6 | 60.8 | 73.1 | 85.3 | 9041 | 9221 | 9402 | 9582 | 9927 | 0.32 |  | 5.2% | 390.5 | 501.7043 | 614.2005 | 729.8451 | 846.7455 | 9.9267 | -0.00032356 | 10.6678 | 0.7411
| Kahe_5 | K5 | LSFO | 569.7 | 54.7 | 74.6 | 94.5 | 114.4 | 134.3 | 9012 | 9133 | 9254 | 9375 | 9691 | 0.32 |  | 3.2% | 569.7 | 749.0388 | 930.7855 | 1114.9401 | 1301.5026 | 9.691 | 9.6798e-06 | 10.6678 | 0.97677
| Kahe_6 | K6 | LSFO | 579.7 | 54 | 74.1 | 94.2 | 114.3 | 134.4 | 9142 | 9450 | 9759 | 10067 | 10059 | 0.32 |  | 2.1% | 579.7 | 763.4542 | 953.3992 | 1149.5551 | 1351.9018 | 10.0588 | -0.00020685 | 10.6678 | 0.60898
| Kalaeloa_CC1 | Kal1 | LSFO | 637.3 | 67 | 72.8 | 78.5 | 84.3 | 90 | 5725 | 5832 | 5939 | 6047 | 8585 | 6 |  | 1.5% | 637.3 | 670.505 | 703.7474 | 738.1936 | 772.6615 | 8.5851 | 0.00012778 | 5.8762 | -2.7089
| Kalaeloa_CC2 | Kal2 | LSFO | 637.3 | 67 | 72.8 | 78.5 | 84.3 | 90 | 5725 | 5832 | 5939 | 6047 | 8585 | 6 |  | 1.5% | 637.3 | 670.505 | 703.7474 | 738.1936 | 772.6615 | 8.5851 | 0.00012778 | 5.8762 | -2.7089
| Kalaeloa_CC3 | Kal3 | LSFO | 0.1 | 0 | 28 |  |  |  | 8651 |  |  |  | 8654 | 6 |  | 1.5% | 0.1 | 242.328 | 242.328 | 242.328 | 242.328 | 8.6546 | 0.00057143 | 5.8762 | -2.7784
| AES | AES | Coal | 1284.7 | 67 | 180 |  |  |  | 6085.2472 |  |  |  | 10957.4052 | 2 |  | 1.5% | 1284.7 | 1972.3329 | 1972.3329 | 1972.3329 | 1972.3329 | 10.9574 | 0 | 10.9574 | 0
| H-Power | HPOWER | MSW | [11 empty] | 18 |  | 10% | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| CIP_CT | CIP-CT1 | Diesel | 714.5 | 45 | 113 |  |  |  | 8915.3529 |  |  |  | 11688 | 40.76 |  | 15% | 714.5 | 1320.744 | 1320.744 | 1320.744 | 1320.744 | 11.688 | 0 | 17.1082 | 5.4202
| Airport_DSG | AiportDG | Biodiesel | 81.64 | 8 | [8 empty] | 10205 | 37.46 |  | 58% | 81.64 | 81.64 | 81.64 | 81.64 | 81.64 | 10.205 | 0 | 9.4073 | -0.79772
| Hawaii_Cogen | Hawaii_Cogen | LSFO | 57.8147 | 12.2 | [8 empty] | 4738.9078 |  |  | 0% | 57.8147 | 57.8147 | 57.8147 | 57.8147 | 57.8147 | 4.7389 | 0 | 4.7389 | 0
| Tesoro_Hawaii | Tesoro_Hawaii | LSFO | 92.8436 | 20 | [8 empty] | 4642.1791 |  |  | 0% | 92.8436 | 92.8436 | 92.8436 | 92.8436 | 92.8436 | 4.6422 | 0 | 4.6422 | 0
Note: horizontal block (technology_info) describes existing thermal technologies to add to technology and project tables (one-to-one); vertical block (build_info) describes build dates for those projects and others defined in PSIP workbook (costs should be provided if build date is earlier than costs in PSIP workbook) | [35 empty] | **** need to make this come out right using Switch heat rate, not actual heat rate…
Note: any values specified here set upper and lower bounds on construction in that year; this will lock in a building plan if applied during the study period. | [29 empty] | PPA true-ups (2018 data in 2018$) |  |  |  |  | verify
gen_install_plan | load_zone | technology | project_name | site | orientation | build_year | proj_existing_cap | proj_overnight_cost | proj_fixed_om | latitude | longitude | retirement year | unit_size | substation_cost_per_kw | variable_o_m | forced_outage_rate | scheduled_outage_rate | fuel | heat_rate | intermittent | resource_limited | distributed | must_run | non_cycling | baseload | cogen | min_uptime | min_downtime | startup_energy |  | project | PPA $/kWh | MWh output | MMBtu input | $/MMBtu | total op cost | cap factor | heat rate | $/kWh no cap | $/kWh incl cap
existing | Oahu | Honolulu_8 | Honolulu 8 | na | na | 1954 | 53.4 | 530.5872 | 9.8583 |  |  | 2014 | 53.4 | 0 | 9.6723 | 0.151 | 0 | LSFO | 11265 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 3 | 5 | 190 |  | Honolulu_8
existing | Oahu | Honolulu_9 | Honolulu 9 | na | na | 1957 | 54.4 | 530.5872 | 9.8583 |  |  | 2014 | 54.4 | 0 | 9.6723 | 0.151 | 0 | LSFO | 11400 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 3 | 5 | 190 |  | Honolulu_9
existing | Oahu | Waiau_3 | Waiau 3 | na | na | 1947 | 46.6 | 530.5872 | 9.8583 |  |  | 2024 | 46.6 | 0 | 9.6723 | 0.15 | 0 | LSFO | 11904 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 3 | 5 | 337 |  | Waiau_3 |  | 963129 | 10602621 |  |  | 2.3594 | 11.0085
existing | Oahu | Waiau_4 | Waiau 4 | na | na | 1950 | 46.6 | 530.5872 | 9.8583 |  |  | 2024 | 46.6 | 0 | 9.6723 | 0.12 | 0 | LSFO | 11832 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 3 | 5 | 337 |  | Waiau_4 | [6 empty] | 11.0085
existing | Oahu | Waiau_5 | Waiau 5 | na | na | 1959 | 54.5 | 530.5872 | 9.8583 |  |  | 2027 | 54.5 | 0 | 9.6723 | 0.047 | 0 | LSFO | 11526 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 3 | 5 | 277 |  | Waiau_5 | [6 empty] | 11.0085
existing | Oahu | Waiau_6 | Waiau 6 | na | na | 1961 | 53.5 | 530.5872 | 9.8583 |  |  | 2027 | 53.5 | 0 | 9.6723 | 0.047 | 0 | LSFO | 11618 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 3 | 5 | 277 |  | Waiau_6 | [6 empty] | 11.0085
existing | Oahu | Waiau_7 | Waiau 7 | na | na | 1966 | 82.9 | 530.5872 | 9.8583 |  |  | 2032 | 82.9 | 0 | 9.6723 | 0.052 | 0 | LSFO | 10600 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 3 | 6 | 933 |  | Waiau_7 | [6 empty] | 11.0085
existing | Oahu | Waiau_8 | Waiau 8 | na | na | 1968 | 86.1 | 530.5872 | 9.8583 |  |  | 2032 | 86.1 | 0 | 9.6723 | 0.052 | 0 | LSFO | 10204 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 3 | 6 | 933 |  | Waiau_8 | [6 empty] | 11.0085
existing | Oahu | Waiau_9 | Waiau 9 | na | na | 1973 | 52.9 | 530.5872 | 17.4846 |  |  | 2050 | 52.9 | 0 | 0.18601 | 0.109 | 0 | Diesel | 13115 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 36 |  | Waiau_9 |  | 20766 | 527369 |  |  | 0.044812 | 25.3958
existing | Oahu | Waiau_10 | Waiau 10 | na | na | 1973 | 49.9 | 530.5872 | 17.4846 |  |  | 2050 | 49.9 | 0 | 0.18601 | 0.109 | 0 | Diesel | 12499 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 33 |  | Waiau_10 | [6 empty] | 25.3958
existing | Oahu | Kahe_1 | Kahe 1 | na | na | 1963 | 82.1 | 530.5872 | 9.8583 |  |  | 2036 | 82.1 | 0 | 9.6723 | 0.036 | 0 | LSFO | 10101 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 3 | 6 | 933 |  | Kahe_1 |  | 2446469 | 26098384 |  |  | 3.4017 | 10.6678
existing | Oahu | Kahe_2 | Kahe 2 | na | na | 1964 | 82.1 | 530.5872 | 9.8583 |  |  | 2036 | 82.1 | 0 | 9.6723 | 0.036 | 0 | LSFO | 9915 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 3 | 6 | 933 |  | Kahe_2 | [6 empty] | 10.6678
existing | Oahu | Kahe_3 | Kahe 3 | na | na | 1970 | 86.1 | 530.5872 | 9.8583 |  |  | 2040 | 86.1 | 0 | 9.6723 | 0.052 | 0 | LSFO | 9703 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 3 | 6 | 933 |  | Kahe_3 | [6 empty] | 10.6678
existing | Oahu | Kahe_4 | Kahe 4 | na | na | 1972 | 85.3 | 530.5872 | 9.8583 |  |  | 2040 | 85.3 | 0 | 9.6723 | 0.052 | 0 | LSFO | 9927 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 3 | 6 | 933 |  | Kahe_4 | [6 empty] | 10.6678
existing | Oahu | Kahe_5 | Kahe 5 | na | na | 1974 | 134.3 | 530.5872 | 9.8583 |  |  | 2045 | 134.3 | 0 | 9.6723 | 0.032 | 0 | LSFO | 9691 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 3 | 6 | 1352 |  | Kahe_5 | [6 empty] | 10.6678
existing | Oahu | Kahe_6 | Kahe 6 | na | na | 1981 | 134.4 | 530.5872 | 9.8583 |  |  | 2045 | 134.4 | 0 | 9.6723 | 0.021 | 0 | LSFO | 10059 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | 3 | 6 | 2703 |  | Kahe_6 | [6 empty] | 10.6678
existing | Oahu | Kalaeloa_CC1 | Kalaeloa CC1 | na | na | 1989 | 90 | 639.8615 | 42.4094 |  |  | 2055 | 90 | 0 | 0.74402 | 0.015 | 0 | LSFO | 8585 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 3 | 5 | 800 |  | Kalaeloa_CC1 | 0.1203 | 78107.4519 | 458973.6058 | 12.2313 | 9651786.106 | 0.099071 | 5.8762 | 0.12357 | 0.17068
existing | Oahu | Kalaeloa_CC2 | Kalaeloa CC2 | na | na | 1991 | 90 | 639.8615 | 42.4094 |  |  | 2055 | 90 | 0 | 0.74402 | 0.015 | 0 | LSFO | 8585 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 3 | 5 | 800 |  | Kalaeloa_CC2 | 0.1203 | 78107.4519 | 458973.6058 | 12.2313 | 9651786.106 | 0.099071 | 5.8762 | 0.12357 | 0.1708
existing | Oahu | Kalaeloa_CC3 | Kalaeloa CC3 | na | na | 1991 | 28 | 639.8615 | 42.4094 |  |  | 2055 | 28 | 0 | 0.74402 | 0.015 | 0 | LSFO | 8654 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 3 | 0 |  | Kalaeloa_CC3 | 0.1203 | 24300.0962 | 142791.7885 | 12.2313 | 3002777.8996 | 0.099071 | 5.8762 | 0.12357 | 0.1708
existing | Oahu | AES | AES | na | na | 1993 | 180 | 2213.4742 | 75.3325 |  |  | 2023 | 180 | 0 | 3.5341 | 0.015 | 0.09667 | Coal | 10957.4052 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 24 | 24 | 0 |  | AES | 0.0559 | 1326641 | 14536543 | 3.8293 | 74681388.4631 | 0.84135 | 10.9574 | 0.056294 | 0.07903
existing | Oahu | H-Power | H-Power | na | na | 1989 | 73 | 2544.3257 | 75.3325 |  |  | 2050 | 73 | 0 | 144.8331 | 0.1 | 0.4137 | MSW | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 |  |  | H-Power | 0.1954 | 397634 | 0 | 0 | 65743494.9074 | 0.62181 | 0 | 0.16534 | 0.1954
existing | Oahu | CIP_CT | CIP CT | na | na | 2009 | 113 | 530.5872 | 13.8574 |  |  | 2070 | 113 | 0 | 4.0851 | 0.15 | 0 | Diesel | 11688 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 126 |  | CIP_CT |  | 34207 | 585220 |  |  | 0.034557 | 17.1082
existing | Oahu | Airport_DSG | Airport DSG | na | na | 2013 | 8 | 530.5872 | 7.7776 |  |  | 2074 | 8 | 0 | 16.375 | 0.58 | 0 | Biodiesel | 10205 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 |  | Airport_DSG |  | 604 | 5682 |  |  | 0.0086187 | 9.4073
existing | Oahu | Hawaii_Cogen | Hawaii Cogen | na | na | 1982 | 12.2 | 511.5172 | 17.4846 |  |  | 2045 | 12.2 | 0 | 54.756 | 0 | 0.13219 | LSFO | 4738.9078 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 |  | Hawaii Cogen | 0.11742 | 92745 | 439510 | 12.2313 | 10890006.7749 | 0.86781 | 4.7389 | 0.11742 | 0.12174
existing | Oahu | Tesoro_Hawaii | Tesoro Hawaii | na | na | 1990 | 20 | 511.5172 | 17.4846 |  |  | 2045 | 20 | 0 | 55.207 | 0 | 0.12398 | LSFO | 4642.1791 | 0 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 |  | Tesoro Hawaii | 0.11668 | 153479 | 712477 | 12.2313 | 17908425.3967 | 0.87602 | 4.6422 | 0.11668 | 0.12103
existing | Oahu | OnshoreWind | Kahuku wind |  |  | 2011 | 30 | 6105.4515 | 48.42 | 21.682 | -157.976 | 2041 | [18 empty] | Kahuku wind | 0.2055 | 74842 |  |  | 1513698.8689 | 0.28479 |  | 0.020225 | 0.2055
existing | Oahu | OnshoreWind | Kawailoa wind |  |  | 2012 | 69 | 4607.7484 | 48.42 | 21.62 | -158.048 | 2042 | [18 empty] | Kawailoa wind | 0.219 | 125802 |  |  | 3481507.3984 | 0.20813 |  | 0.027674 | 0.219
existing | Oahu | CentralTrackingPV | Kapolei Solar Energy Park |  |  | 2012 | 1 | 5570.2165 | 22.46 | 21.3159 | -158.1053 | 2042 | [18 empty] | Kapolei Solar Energy Park | 0.236 | 1886 |  |  | 23404.7065 | 0.2153 |  | 0.01241 | 0.236
existing | Oahu | CentralTrackingPV | Pearl City Peninsula Solar Park |  |  | 2012 | 1 | 5640.1159 | 22.46 | 21.3768 | -157.9684 | 2042
existing | Oahu | CentralTrackingPV | Kalaeloa Solar Two |  |  | 2012 | 5 | 5710.0153 | 22.46 | 21.32 | -158.0869 | 2042 | [18 empty] | Kalaeloa Solar Two | 0.2183 | 10437 |  |  | 117023.5323 | 0.23829 |  | 0.011212 | 0.2183
existing | Oahu | CentralTrackingPV | Kalaeloa Renewable Energy Park |  |  | 2014 | 5 | 4475.8182 | 22.46 | 21.3228 | -158.0443 | 2044 | [18 empty] | Kalaeloa Renewable Energy Park | 0.216 | 8385.3 |  |  | 117023.5323 | 0.19145 |  | 0.013956 | 0.216
existing | Oahu | CentralTrackingPV | Waihonu South Solar |  |  | 2016 | 1.5 | 4094.3929 | 22.46 | 21.4689 | -158.0164 | 2046 | [18 empty] | Waihonu South Solar | 0.145 | 63455.12 |  |  | 35107.0597 | 4.8292 |  | 0.00055326 | 0.0078804
existing | Oahu | CentralTrackingPV | Waihonu North Solar |  |  | 2016 | 5 | 4094.3929 | 22.46 | 21.4706 | -158.0133 | 2046 | [18 empty] | Waihonu North Solar | 0.145 | 63455.12 |  |  | 117023.5323 | 1.4487 |  | 0.0018442 | 0.026268
existing | Oahu | CentralTrackingPV | EE Waianae Solar Project |  |  | 2017 | 27.6 | 4094.3929 | 22.46 | 21.4619 | -158.1893 | 2047 | [18 empty] | EE Waianae Solar Project | 0.145 | 63455.12 |  |  | 645969.8981 | 0.26245 |  | 0.01018 | 0.145
existing | Oahu | CentralTrackingPV | Aloha Solar Energy Fund 1 PK1 |  |  | 2017 | 5 | 4094.3929 | 22.46 | 21.4069 | -158.1514 | 2047 | [18 empty] | Aloha Solar Energy Fund 1 PK1 | 0.145 | 63455.12 |  |  | 117023.5323 | 1.4487 |  | 0.0018442 | 0.026268
existing | Oahu | IC_Schofield | IC Schofield | na | na | 2018 | 48.84 |  |  |  |  | 2048 | [18 empty] | IC Schofield |  | 31231 | 272164 |  |  | 0.072997 | 8.7145
existing | Oahu | CentralTrackingPV | Lanikuhana Solar |  |  | 2019 | 14.7 |  |  | 21.4262 | -158.0185 | 2049
existing | Oahu | CentralTrackingPV | West Loch PV |  |  | 2019 | 20 |  |  | 21.3376 | -158.0107 | 2049
existing | Oahu | CentralTrackingPV | Waipio PV |  |  | 2019 | 45.9 |  |  | 21.4306 | -157.9946 | 2049
existing | Oahu | CentralTrackingPV | Kawailoa Solar |  |  | 2019 | 49 |  |  | 21.6363 | -158.0608 | 2049
existing | Oahu | SlopedDistPV | Sloped DGPV |  |  | 2013 | 70.21 | 6126.9116 | 0
existing | Oahu | SlopedDistPV | Sloped DGPV |  |  | 2014 | 73.44 | 6126.9116 | 0
existing | Oahu | SlopedDistPV | Sloped DGPV |  |  | 2015 | 45.96 | 6126.9116 | 0
existing | Oahu | SlopedDistPV | Sloped DGPV |  |  | 2016 | 26.48 | 6126.9116 | 0
existing | Oahu | SlopedDistPV | Sloped DGPV |  |  | 2017 | 34.62 | 6126.9116 | 0
existing | Oahu | SlopedDistPV | Sloped DGPV |  |  | 2018 | 20.37
existing | Oahu | SlopedDistPV | Sloped DGPV |  |  | 2019 | 16.74
existing | Oahu | SlopedDistPV | Sloped DGPV |  |  | 2020 | 15.48
existing | Oahu | FlatDistPV | Flat DGPV |  |  | 2013 | 48.79 | 4207.7087 | 0
existing | Oahu | FlatDistPV | Flat DGPV |  |  | 2014 | 28.56 | 4207.7087 | 0
existing | Oahu | FlatDistPV | Flat DGPV |  |  | 2015 | 16.04 | 4207.7087 | 0
existing | Oahu | FlatDistPV | Flat DGPV |  |  | 2016 | 33.52 | 4207.7087 | 0
existing | Oahu | FlatDistPV | Flat DGPV |  |  | 2017 | 33.38 | 4207.7087 | 0
existing | Oahu | FlatDistPV | Flat DGPV |  |  | 2018 | 70.63
existing | Oahu | FlatDistPV | Flat DGPV |  |  | 2019 | 14.26
existing | Oahu | FlatDistPV | Flat DGPV |  |  | 2020 | 125.52
End-of-year distributed PV capacity from quarterly HECO reports for Oahu
https://www.hawaiianelectric.com/clean-energy-hawaii/our-clean-energy-portfolio/quarterly-installed-solar-data
e.g., https://www.hawaiianelectric.com/documents/clean_energy_hawaii/clean_energy_facts/pv_summary_4Q_2019.pdf
mid-year values, not used
start of year | end of year | MW | % residential | % commercial | residential additions | commercial additions |  |  | mid-year | MW | % residential | % commercial
2013 | 2012 | 119 | 0.59 | 0.41 | 70.21 | 48.79 |  |  | 2012 | 90.6 | 0.59 | 0.41
2014 | 2013 | 221 | 0.65 | 0.35 | 73.44 | 28.56 |  |  | 2013 | 170 | 0.65 | 0.35
2015 | 2014 | 283 | 0.67 | 0.33 | 45.96 | 16.04 |  |  | 2014 | 254 | 0.67 | 0.33
2016 | 2015 | 343 | 0.63 | 0.37 | 26.48 | 33.52 |  |  | 2015 | 310 | 0.64 | 0.36
2017 | 2016 | 411 | 0.61 | 0.39 | 34.62 | 33.38 |  |  | 2016 | 371 | 0.64 | 0.36
2018 | 2017 | 502 | 0.54 | 0.46 | 20.37 | 70.63 |  |  | 2017 | 480 | 0.55 | 0.45
2019 | 2018 | 533 | 0.54 | 0.46 | 16.74 | 14.26 |  |  | 2018 | 519 | 0.54 | 0.46
2020 | 2019 | 674 | 0.45 | 0.55 | 15.48 | 125.52 |  |  | 2019 | 547 | 0.54 | 0.46
Projects below are feed-in-tariff projects, so seem to be included in DER adoption, not individual projects
existing | Oahu | CentralTrackingPV | Mauka FIT 1 |  |  | 2020 | 3.5
existing | Oahu | CentralTrackingPV | Aloha Solar Energy Fund II |  |  | 2020 | 5 |  |  | 21.3035 | -158.0598
Note: the rows below are unused; these were moved back into the PSIP module.
Oahu DistPV construction calculations, assuming 20-year life |  |  |  | see p. 3-8 of PSIP 2016-12-23 vol. 1. for 20-year life and discussion of reconstruction at retirement (focused on utility-scale, but we assume it applies to DG; also Resolve applied these as set levels).
year | non-controllable | controllable | total level | retirements | additions |  | All-islandPV level forecast from H-1 of PSIP 2016-12-23 and xx | Approx. Oahu PV level from Figure J-10 of 2016-12-23 PSIP (excl FIT(?))
2016 | #REF! | 0 | #REF! | 0 |  |  | 471 | 400 |  | DistPV installations
2020 | 606.3 | 0 | 606.3 | 0 | #REF! |  | 856 | 600 |  | #REF!
2022 | 606.3 | 74 | 680.3 | 0 | 74 |  |  |  |  | (2022, "DistPV", 74),
2025 | 606.3 | 138.6 | 744.9 | 0 | 64.6 |  | 1169 | 720 |  | (2025, "DistPV", 64.6),
2030 | 606.3 | 262.4 | 868.7 | 0 | 123.8 |  |  | 865 |  | (2030, "DistPV", 123.8),
2035 | 606.3 | 409.1 | 1015.4 | 0 | 146.7 |  |  | 1020 |  | (2035, "DistPV", 146.7),
2040 | 606.3 | 557.1 | 1163.4 | #REF! | #REF! |  | 1517 | 1160 |  | #REF!
2045 | 606.3 | 701.6 | 1307.9 | 138.6 | 283.1 |  | 1697 | 1300 |  | (2045, "DistPV", 283.1),
optional replacements at retirement (pasted into PSIP module)
(2011, "OnshoreWind", 30),
(2012, "OnshoreWind", 69),
(2012, "CentralTrackingPV", 5),
(2017, "CentralTrackingPV", 27.6),
#REF!
(2018, "IC_Schofield", 48.84),
(2019, "CentralTrackingPV", 49),
(2019, "CentralTrackingPV", 14.7),
(2019, "CentralTrackingPV", 45.9),
#REF!
TODO: re-import HECO generator info with 20 year life for renewables
TODO: make sure import code can handle multiple batches of the same technology in the same year, with or without different locations (or none at all)
TODO: convert LoadShiftBattery to some standard tech (check what HECO assumed)
TODO: no reserves from LoadShiftBattery in PSIP?
TODO: any contingency or regulation battery in PSIP?
TODO: allow central PV and wind without lat lon specified (just require a certain total amount from any appropriate project)
TODO: switch to using 4-hour and 6-hour batteries, and fix up LoadShiftBattery
TODO: add project size and cap factors for West Loch PV (on Pearl Harbor land) (eventually; can use nearest ag land solar for now)
TODO: add gen_install_plan to scenario_data (default is "existing"); then we can include PSIP_DistPV to follow the forecast or exclude it to allow free selection of PV
note: project build data will get stored in one built_project table,but scenario_data.py will extract it into proj_existing_builds.tab and proj_build_costs.tab
Notes:
Honua was removed because the company behind it went bankrupt in Feb. 2016 without completing the project. see:
Star-Advertiser "Pulling the Plug", 2016-02-08, http://www.pressreader.com/usa/honolulu-star-advertiser/20160208/281848642645296
http://www.ct-si.org/events/APCE2011/sld/pdf/9.pdf
http://oeqc.doh.hawaii.gov/Shared%20Documents/EA_and_EIS_Online_Library/Oahu/2010s/2010-04-08-OA-FEA-Honua-Power.pdf
TODO:
report reserves provided by each source
jdfvbkmnjjjuhjuhnbvcxzp,lmpn/////[
.,?"P}o?P<K?"<K?"op]k?"PKOP']/K<"}¦OPKPO"}<K?"KL,l?"LK?"K<">K?">L
TODO later:
add code to support non_cycling flag in switch unit commitment
limit Airport DSG to 1500 hours/year
add Tesoro cogen plant (built in 1983; assume 61-year life)
add Chevron cogen plant (G1-G3 built in 1990, G4 built in 2011; assume 61-year life)
fill in capital costs for all plants (use original cost, converted to 2016$; this reflects the fact that payments escalate with inflation in switch)
get better fixed and variable O&M for all plants
In Ulupono scenarios, switch wind and solar to 35-year life to avoid retirement and replacement by 2045
include pumped storage in reserve requirements and provision
allow specification of O&M per hour (based on commitment), rather than just per MWh (based on dispatch)
create flag for cost-only projects (not committed/dispatched, just built/retired)
convert batteries, hydrogen, evs? and fuel market expansion into projects with side constraints imposed by modules
define multiple speeds of regulating reserve product, with separate targets at each speed (to account for renewable mis-forecast)
(we don't define a contingency reserve product for extreme misforecasts, because it is hard to bound the quantity, and it can be a slow-start product (not instant-start), and most likely it would be addressed by rolling blackouts, not dipping into n-1 reserves)
allow users to specify a "greenfield" model, omitting all previous builds (in scenario_data.py)
Note on C2: converts O&M costs in 1987$ to 2016$, based on Q1 values of GDP deflator shown at https://fred.stlouisfed.org/series/GDPDEF
Note on D2: converts O&M costs in 1987$ to 2016$, based on Q1 values of GDP deflator shown at https://fred.stlouisfed.org/series/GDPDEF
Note on E2: converts O&M costs in 1987$ to 2016$, based on Q1 values of GDP deflator shown at https://fred.stlouisfed.org/series/GDPDEF
Note on F2: converts O&M costs in 1987$ to 2016$, based on Q1 values of GDP deflator shown at https://fred.stlouisfed.org/series/GDPDEF
Note on P16: converted hourly cost to cost per MWh, assuming operation in middle of range
Note on Z16: Actual heat rate in 2018 was much higher than HSIS but cap factor was very low, so HSIS remains (more) plausible. So we stick with HSIS.
Note on P17: converted hourly cost to cost per MWh, assuming operation in middle of range
Note on Z17: Actual heat rate in 2018 was much higher than HSIS but cap factor was very low, so HSIS remains (more) plausible. So we stick with HSIS.
Note on P24: From p. 18 of Coffman UHERO report at http://uhero.hawaii.edu/assets/WP_2014-5.pdf
Note on G27: Changed from 185 to 180 to match GE RPS Study (http://www.hnei.hawaii.edu/projects/hawaii-rps-study) and EIA form 860 data for 2017.
Note on K27: In May 2020, we switched from GE HSIS heat rate (shown in table to right) to this value, to match actual average heat rate reported for 2018, since actual heat rate is much lower than GE and matches PPA better. Also switched to single-step heat rate curve since we don't know the shape well (keeping min load and min-load power from HSIS).
Note on O27: In May 2020, we switched from GE HSIS heat rate (shown in table to right) to this value, to match actual average heat rate reported for 2018, since actual heat rate is much lower than GE and matches PPA better. Also switched to single-step heat rate curve since we don't know the shape well (keeping min load and min-load power from HSIS).
Note on P27: From p. 18 of Coffman UHERO report at http://uhero.hawaii.edu/assets/WP_2014-5.pdf
Note on E28: Removed heat rate (74014!) because it runs on waste, which is a non-fuel in SWITCH-Hawaii.
Note on G28: removed 73 MW operating point because we don't use a heat rate curve for MSW (treat as non-fuel energy source)
Note on P28: From p. 18 of Coffman UHERO report at http://uhero.hawaii.edu/assets/WP_2014-5.pdf
Note on C29: This is Siemens SGT6-3000E per final order in docket 2005-0145
Note on D29: We switched from Biodiesel to Diesel May 2020 (but Switch was allowing diesel before then anyway). Labeled as biodiesel-only in HSIS and https://www.hawaiianelectric.com/clean-energy-hawaii/our-clean-energy-portfolio/renewable-energy-sources/biofuels But in RESOLVE modeling for 2016 PSIP, HECO modeled it as diesel until 2045 then biodiesel. EIA form 923 says it ran on biodiesel before Nov. 2018, then diesel after (at least till the start of 2020, maybe longer).
Note on K29: Assigned a value to make consistent with full-load heat rate
Note on Z29: Actual heat rate in 2018 was much higher than HSIS but cap factor was very low, so HSIS remains (more) plausible. So we stick with HSIS.
Note on E30: Changed from 40.8 to be consistent with 8 MW min/max load and 10,205 full load heat rate
Note on F30: Changed from 0 because HECO can only run gen at 8 MW (and only 1500 h/y) per application (p. 23) in docket 2008-0329
Note on K30: removed 10,205 from here because it has no corresponding power point
Note on D31: Mainly burns "other gases" and waste oil, but we represent it as LSFO
Note on E31: Based on total fuel used for electricity production in 2018 EIA Form 923
Note on F31: 3 x 3.0 MW and 1 x 3.2 MW according to EIA form 860, but we model as a single unit Modeled as running only at full capacity (derated by outage rate) to force baseload operation (otherwise, with baseload flag, Switch forces commitment but allows free dispatch within allowed range)
Note on D32: Mainly burns waste oil, but we represent it as LSFO
Note on E32: Based on total fuel used for electricity production in 2018 EIA Form 923
Note on F32: Modeled as running only at full capacity (derated by outage rate) to force baseload operation (otherwise, with baseload flag, Switch forces commitment but allows free dispatch within allowed range)
Note on D37: Not used in Switch but useful for documentation.
Note on E37: site and orientation for existing renewable projects will be looked up in import_data.py
Note on F37: site and orientation for existing renewable projects will be looked up in import_data.py
Note on G37: from EIA 860 or 923 database unless otherwise noted
Note on H37: Despite the name, this is actually the amount of capacity added in each project in the specified year.
Note on I37: $/kW, can be omitted if technology and build_year are covered by the new generator costs workbook
Note on J37: $/kW-year Can be omitted if technology and build_year are covered by the new generator costs workbook For pre-2000 plants, this is taken from Assumptions to AEO 1996 (earliest available) and converted from 1987$ to 2016$. For newer plants, we use values from matching year of Assumptions to AEO. Before November 2019 we used $0 for fixed O&M (unrealistic).
Note on K37: If latitude and longitude are specified, they are used to match existing renewable projects to available resources and/or to calculate spur line cost to interconnect; if omitted, spur line cost will be assumed 0.
Note on M37: assumed unavailable in retirement year Unless otherwise noted, these are the latest dates in either the "E3 Plan" or "E3 Plan with Generation Modernization" from the 2016-12-31 PSIP. Effectively that means the Gen Mod dates except Kahe 5 & 6, which are from the base plan. Note that "HECO construction plan 2020-03-17.docx" is the same as the Gen Mod plan.
Note on P37: $/MWh For pre-2000 plants, this is taken from Assumptions to AEO 1996 (earliest available) and converted from 1987$ to 2016$. For newer plants, we use values from matching year of Assumptions to AEO. Before November 2019 we used the unrealistically low numbers from HSIS (and $0 for fixed O&M).
Note on Q37: Currently ignored in switch_model.hawaii.scenario_data, so we just use scheduled_outage_rate to adjust output of baseload generators.
Note on T37: full load heat rate, Btu/kWh
Note on X37: closest match to HECO's definition of "baseload" -- must be committed, but level can be adjusted. This can be enabled or ignored in hawaii.scenario_data from Hawaii RPS Study, GE Energy Management Energy Consulting. 8.2 Thermal Generating Characteristics, Table 7: Thermal Generating Unit Properties
Note on Y37: Must be fully committed or fully non-committed during each timeseries (day). This is not currently implemented.
Note on Z37: forces dispatch at 100% unless otherwise specified
Note on AB37: From GE Hawaii RPS Study for HNEI, 2015, https://www.hnei.hawaii.edu/projects/hawaii-rps-study
Note on AC37: From GE Hawaii RPS Study for HNEI, 2015, https://www.hnei.hawaii.edu/projects/hawaii-rps-study
Note on AD37: MMBtu, for whole unit Used hot values from Hawaii RPS Study
Note on AG37: from p. 66 of https://puc.hawaii.gov/wp-content/uploads/2018/12/FY18-PUC-Annual-Report_FINAL.pdf
Note on AH37: From EIA form 923 for 2018
Note on AI37: From EIA form 923 for 2018
Note on AJ37: From AEO_2019_Reference scenario in back-end database for most common fuel reported by EIA (coal/LSFO)
Note on I38: $/kW; 2016 annual report says total ratebase is $1386000000, which is about half generation, so we set value per kW accordingly This is probably a terrible idea, because we should amortize the first-year book value, not the mid-life book value. But we never use existing-plant capital costs for anything so it's OK for now.
Note on M38: deactivated 1/31/14 according to p. 2 of AOC reportsfor 2014-2019 at https://puc.hawaii.gov/reports/energy-reports/adequacy-of-supply/
Note on M39: deactivated 1/31/14 according to p. 2 of AOC reportsfor 2014-2019 at https://puc.hawaii.gov/reports/energy-reports/adequacy-of-supply/
Note on M40: Was slated for deactivation at end of 2016 according to 2014 and 2015 AOC reports and end of 2017 according to 2016 AOC report, but then isn't mentioned in 2017-2019 AOC reports. No retiremnet date shown in EIA form 860 for 2018. We assume it stays in service through 2023 per "HECO construction plan 2020-03-17.docx". See AOC reports at https://puc.hawaii.gov/reports/energy-reports/adequacy-of-supply/
Note on M41: Was slated for deactivation at end of 2016 according to 2014 and 2015 AOC reports and end of 2017 according to 2016 AOC report, but then isn't mentioned in 2017-2019 AOC reports. No retiremnet date shown in EIA form 860 for 2018. We assume it stays in service through 2023 per "HECO construction plan 2020-03-17.docx". See AOC reports at https://puc.hawaii.gov/reports/energy-reports/adequacy-of-supply/
Note on M46: set to 2050 since the plan says it will switch to biodiesel in 2045
Note on M47: set to 2050 since the plan says it will switch to biodiesel in 2045
Note on I54: From Assumptions to the Annual Energy Outlook 1996 (earliest available), converted from 1987$ to 2016$. Note that the 2018 PPA reported by PUC (which excludes capacity payments) almost exactly covers O&M and fuel, so we assume this is an appropriate proxy for the capacity payment.
Note on M54: set to 2055 (slightly longer than 61-year age of existing units) so it is available in 2045 or 2050 scenarios.
Note on X54: This is handled by hawaii.oahu_plants
Note on I55: From Assumptions to the Annual Energy Outlook 1996 (earliest available), converted from 1987$ to 2016$. Note that the 2018 PPA reported by PUC (which excludes capacity payments) almost exactly covers O&M and fuel, so we assume this is an appropriate proxy for the capacity payment.
Note on M55: set to 61 years, based on average age of already-scheduled retirements
Note on I56: From Assumptions to the Annual Energy Outlook 1996 (earliest available), converted from 1987$ to 2016$. Note that the 2018 PPA reported by PUC (which excludes capacity payments) almost exactly covers O&M and fuel, so we assume this is an appropriate proxy for the capacity payment.
Note on M56: set to 61 years, based on average age of already-scheduled retirements
Note on G57: Started 10/10/92, so we count it as the start of 1993, so it continues to end of 2022.
Note on I57: From Assumptions to the Annual Energy Outlook 1996 (earliest available), converted from 1987$ to 2016$. Note that the 2018 PPA reported by PUC (which excludes capacity payments) almost exactly covers O&M and fuel, so we assume this is an appropriate proxy for the capacity payment.
Note on M57: set to 30 years (expiry of initial PPA) starting 2019-10-01 because there is no support from PUC, HECO or stakeholders for continuing with coal and continuing with biomass is economically marginal (biomass could burn as well in HECO plants and that's probably easier politically, but we don't generally consider that option). "HECO construction plan 2020-03-17.docx" also says it will be retired in 9/2022.
Note on R57: Derated to match average capacity factor in 2012-16 from EIA form 923
Note on Z57: Treated as baseload starting June 2020 to enforce upper limit on production, matching historical capacity factor. This may give better match to HECO's historical usage patterns.
Note on AB57: AES PPA states that HECO must reimburse resetart costs if plant operation is suspended more than 5 times in a year. Implied plant must run for long periods at a atime, so we set it to 24 hours.
Note on AC57: AES PPA states that HECO must reimburse resetart costs if plant operation is suspended more than 5 times in a year. Implied plant must run for long periods at a atime, so we set it to 24 hours.
Note on C58: note: nameplate capacity is 97.3 MW and winter/summer capacity are 86.0 MW per EIA form 860M for September 2016
Note on H58: note: nameplate capacity is 97.3 MW and winter/summer capacity are 86.0 MW per EIA form 860M for September 2016
Note on I58: set to get correct PPA price in 2018 when using standard finance assumptions applied in Switch (6% over project life). Previously was set based on 2016 NREL ATB (2190.18 for wind, 2915.91 for solar) or PSIP thermal plants (~$1750/kW), but these PPAs don't match that.
Note on J58: HECO reported 12/12/2019 that this has a capacity cost of up to 17685360/year, so we just divide that by capacity and adjust for inflation.
Note on M58: set to 61 years, based on average age of already-scheduled retirements
Note on R58: 42.8 MW baseload operation per monthly and annual avg production in EIA form 923 for 2015
Note on AB58: Treated as zero, since it runs all the time.
Note on AC58: Treated as zero, since it runs all the time.
Note on AD58: Treated as variable plant instead of fuel-based gen, so startup fuel must be omitted.
Note on M59: set to 61 years, based on average age of already-scheduled retirements
Note on C60: "Airport Dispatchable Standby Generation" (docket 2008-0329)
Note on G60: planned for late 2013 according to https://puc.hawaii.gov/wp-content/uploads/2015/04/Adequacy-of-Supply-HECO-2013.pdf
Note on J60: Assumed same as conventional combustion turbine in assumptions to AEO 2013
Note on M60: set to 61 years, based on average age of already-scheduled retirements
Note on P60: Assumed same as conventional combustion turbine in assumptions to AEO 2013
Note on AD60: RPS Study says 126, same as CIP CT, but that seems like a typo, since this is much smaller and an IC. It is 6x smaller than Schofield IC, so we use 1/6 of Schofield value from RPS Study.
Note on C61: AKA Island Energy Services; omitted until May 2020
Note on H61: from p. 66 of https://puc.hawaii.gov/wp-content/uploads/2018/12/FY18-PUC-Annual-Report_FINAL.pdf EIA Form 860 says 12.2 MW
Note on I61: Assumed same as conventional combustion turbine in assumptions to AEO 1996
Note on J61: Assumed same as conventional combustion turbine in assumptions to AEO 1996
Note on M61: Assumed unviable after 2045.
Note on P61: Adjusted to get 2018 energy cost to match PPA report to PUC
Note on R61: Set to give same output as in 2018 (assumed to operate in baseload mode)
Note on AB61: Treated as zero, since it runs all the time.
Note on AC61: Treated as zero, since it runs all the time.
Note on C62: AKA PAR; omitted until May 2020
Note on G62: 3 3 MW units installed in 1990; 1 3.2 MW unit installed in 2011
Note on H62: from p. 66 of https://puc.hawaii.gov/wp-content/uploads/2018/12/FY18-PUC-Annual-Report_FINAL.pdf EIA form 860 says 20 MW
Note on I62: Assumed same as conventional combustion turbine in assumptions to AEO 1996
Note on J62: Assumed same as conventional combustion turbine in assumptions to AEO 1996
Note on M62: Assumed unviable after 2045.
Note on P62: Adjusted to get 2018 energy cost to match PPA report to PUC
Note on R62: Set to give same output as in 2018 (assumed to operate in baseload mode)
Note on AB62: Treated as zero, since it runs all the time.
Note on AC62: Treated as zero, since it runs all the time.
Note on C63: Kahuku wind farm
Note on I63: set to get correct PPA price in 2018 when using standard finance assumptions applied in Switch (6% over project life). Previously was set based on 2016 NREL ATB (2190.18 for wind, 2915.91 for solar) or PSIP thermal plants (~$1750/kW), but these PPAs don't match that.
Note on J63: From Assumptions to AEO 2019
Note on K63: found via Google Maps search
Note on M63: Not used by Switch, but inserted here to get financing right; must match new-generation workbook.
Note on C64: Kawailoa Wind Farm
Note on I64: set to get correct PPA price in 2018 when using standard finance assumptions applied in Switch (6% over project life). Previously was set based on 2016 NREL ATB (2190.18 for wind, 2915.91 for solar) or PSIP thermal plants (~$1750/kW), but these PPAs don't match that.
Note on J64: From Assumptions to AEO 2019
Note on K64: found via Google Maps search
Note on C65: actually fixed-tilt, but we don't generally model that, so we treat as tracking
Note on D65: AKA Kapolei Sustainable Energy Park
Note on I65: set to get correct PPA price in 2018 when using standard finance assumptions applied in Switch (6% over project life). Previously was set based on 2016 NREL ATB (2190.18 for wind, 2915.91 for solar) or PSIP thermal plants (~$1750/kW), but these PPAs don't match that.
Note on J65: From Assumptions to AEO 2019
Note on K65: Based on address on EIA form 860 (91-290 Malakole Street), confirmed on Google Maps satellite view.
Note on C66: actually fixed-tilt, but we don't generally model that, so we treat as tracking
Note on K66: based on lat/lon in EIA Form 860, adjusted slightly by inspection of Google Maps satellite view
Note on I67: set to get correct PPA price in 2018 when using standard finance assumptions applied in Switch (6% over project life). Previously was set based on 2016 NREL ATB (2190.18 for wind, 2915.91 for solar) or PSIP thermal plants (~$1750/kW), but these PPAs don't match that.
Note on J67: From Assumptions to AEO 2019
Note on K67: location from EIA form 860M database (September 2016)
Note on C68: actually fixed-tilt, but we don't generally model that, so we treat as tracking
Note on I68: set to get correct PPA price in 2018 when using standard finance assumptions applied in Switch (6% over project life). Previously was set based on 2016 NREL ATB (2190.18 for wind, 2915.91 for solar) or PSIP thermal plants (~$1750/kW), but these PPAs don't match that.
Note on J68: From Assumptions to AEO 2019
Note on K68: Found by searching on Google Maps near address in EIA Form 860 (Roosevelt Ave & Essex Road) for land that looked like photos from https://bchdesign.com/portfolio/kalaeloa-renewable-energy/
Note on C69: actually fixed-tilt, but we don't generally model that, so we treat as tracking
Note on K69: From EIA Form 860; not on Google Maps images by June 2020.
Note on C70: actually fixed-tilt, but we don't generally model that, so we treat as tracking
Note on K70: From EIA Form 860; not on Google Maps images by June 2020.
Note on I71: set to get correct PPA price in 2018 when using standard finance assumptions applied in Switch (6% over project life). Previously was set based on 2016 NREL ATB (2190.18 for wind, 2915.91 for solar) or PSIP thermal plants (~$1750/kW), but these PPAs don't match that.
Note on J71: From Assumptions to AEO 2019
Note on K71: Mauka of Kamaile academy according to http://eurusenergy.com/news/press-releases/eurus-energy-america/waianae-solar-project-construction-financing/
Note on C72: actually fixed-tilt, but we don't generally model that, so we treat as tracking
Note on K72: From EIA Form 860; not on Google Maps images by June 2020.
Note on C73: profile copied from PSIP 2016-12 generator and storage data.xlsx
Note on C74: Lanikuhana Solar (Mililani Solar), formerly SunEdison
Note on G74: from https://www.hawaiianelectric.com/clean-energy-hawaii/our-clean-energy-portfolio/renewable-project-status-board
Note on K74: from page source of http://energy.ehawaii.gov/epd/public/energy-project-details.html?rid=f1-3b2df53a54d8c6d3
Note on C75: West Loch PV
Note on G75: Seems like half of it came online in 2017 (or maybe it was some other project at JBPHH?), and all of it was expected to be online in 2018. See https://www.bizjournals.com/pacific/news/2017/04/28/navy-launches-operations-of-pearl-harbor-solar.html and https://dailyenergyinsider.com/news/10294-hawaiian-electric-companies-reports-100-megawatts-solar-installed-across-service-territories-2017/ But according to https://www.hawaiianelectric.com/clean-energy-hawaii/our-clean-energy-portfolio/renewable-project-status-board (accessed 10/22/19) it will be online in 2019.
Note on H75: This is 28 MW DC, 20 MW AC. See PSIP 2016-12-23 and these links: https://www.hawaiianelectric.com/navy-hawaiian-electric-plan-large-solar-project-on-joint-base-pearl-harbor-hickam (most authoritative) https://dailyenergyinsider.com/news/10294-hawaiian-electric-companies-reports-100-megawatts-solar-installed-across-service-territories-2017/ http://greenfleet.dodlive.mil/files/2016/09/JB-Pearl-Harbor-Hickam-Factsheet.pdf https://www.bizjournals.com/pacific/news/2017/04/28/navy-launches-operations-of-pearl-harbor-solar.html
Note on K75: from Pearl Harbor Hickam Solar Project fact sheet at http://greenfleet.dodlive.mil/files/2016/09/JB-Pearl-Harbor-Hickam-Factsheet.pdf
Note on C76: Waipio (Waiawa) PV, formerly SunEdison
Note on G76: from https://www.hawaiianelectric.com/clean-energy-hawaii/our-clean-energy-portfolio/renewable-project-status-board
Note on K76: from page source of http://energy.ehawaii.gov/epd/public/energy-project-details.html?rid=f7-3f29f31d354cf91d
Note on C77: Kawailoa Solar, formerly SunEdison project
Note on G77: from https://www.hawaiianelectric.com/clean-energy-hawaii/our-clean-energy-portfolio/renewable-project-status-board
Note on K77: From xx (view source for map marker)
Note on I78: set equal to 2016 cost in NREL Advanced Technology Baseline (see "PSIP 2016-12 and ATB 2018 generator data.xlsx")
Note on I86: set equal to 2016 cost in NREL Advanced Technology Baseline (see "PSIP 2016-12 and ATB 2018 generator data.xlsx")
Note on G116: Online 4/2/20 according to https://www.hawaiianelectric.com/clean-energy-hawaii/our-clean-energy-portfolio/renewable-project-status-board (accessed 5/25/20).
Note on K116: TMK (1) 9-1-013-070-0000 from KAL 17-007 permit application at https://dbedt.hawaii.gov/hcda/aloha-solar/, location looked up on https://qpublic.schneidercorp.com/Application.aspx?App=HonoluluCountyHI&PageType=Search
Note on C121: from data/HECO Plans/PSIP-WebDAV/2017-01-31 Response to Parties IRs/CA-IR-1/Input and Output Files by Case/E3 and Company Defined Cases/Market DGPV (Reference)/OA_NOLNG/planned_installed_capacities.tab
Note on B122: from data/HECO Plans/PSIP-WebDAV/2017-01-31 Response to Parties IRs/CA-IR-1/Input and Output Files by Case/E3 and Company Defined Cases/Market DGPV (Reference)/OA_NOLNG/planned_installed_capacities.tab
Note on C122: from data/HECO Plans/PSIP-WebDAV/2017-01-31 Response to Parties IRs/CA-IR-1/Input and Output Files by Case/E3 and Company Defined Cases/Market DGPV (Reference)/OA_NOLNG/planned_installed_capacities.tab
Note on B123: from data/HECO Plans/PSIP-WebDAV/2017-01-31 Response to Parties IRs/CA-IR-1/Input and Output Files by Case/E3 and Company Defined Cases/Market DGPV (Reference)/OA_NOLNG/planned_installed_capacities.tab
Note on C123: from data/HECO Plans/PSIP-WebDAV/2017-01-31 Response to Parties IRs/CA-IR-1/Input and Output Files by Case/E3 and Company Defined Cases/Market DGPV (Reference)/OA_NOLNG/planned_installed_capacities.tab
Note on B124: from data/HECO Plans/PSIP-WebDAV/2017-01-31 Response to Parties IRs/CA-IR-1/Input and Output Files by Case/E3 and Company Defined Cases/Market DGPV (Reference)/OA_NOLNG/planned_installed_capacities.tab
Note on C124: from data/HECO Plans/PSIP-WebDAV/2017-01-31 Response to Parties IRs/CA-IR-1/Input and Output Files by Case/E3 and Company Defined Cases/Market DGPV (Reference)/OA_NOLNG/planned_installed_capacities.tab
Note on B125: from data/HECO Plans/PSIP-WebDAV/2017-01-31 Response to Parties IRs/CA-IR-1/Input and Output Files by Case/E3 and Company Defined Cases/Market DGPV (Reference)/OA_NOLNG/planned_installed_capacities.tab
Note on C125: from data/HECO Plans/PSIP-WebDAV/2017-01-31 Response to Parties IRs/CA-IR-1/Input and Output Files by Case/E3 and Company Defined Cases/Market DGPV (Reference)/OA_NOLNG/planned_installed_capacities.tab
Note on B126: from data/HECO Plans/PSIP-WebDAV/2017-01-31 Response to Parties IRs/CA-IR-1/Input and Output Files by Case/E3 and Company Defined Cases/Market DGPV (Reference)/OA_NOLNG/planned_installed_capacities.tab
Note on C126: from data/HECO Plans/PSIP-WebDAV/2017-01-31 Response to Parties IRs/CA-IR-1/Input and Output Files by Case/E3 and Company Defined Cases/Market DGPV (Reference)/OA_NOLNG/planned_installed_capacities.tab
Note on B127: from data/HECO Plans/PSIP-WebDAV/2017-01-31 Response to Parties IRs/CA-IR-1/Input and Output Files by Case/E3 and Company Defined Cases/Market DGPV (Reference)/OA_NOLNG/planned_installed_capacities.tab
Note on C127: from data/HECO Plans/PSIP-WebDAV/2017-01-31 Response to Parties IRs/CA-IR-1/Input and Output Files by Case/E3 and Company Defined Cases/Market DGPV (Reference)/OA_NOLNG/planned_installed_capacities.tab
Note on B128: from data/HECO Plans/PSIP-WebDAV/2017-01-31 Response to Parties IRs/CA-IR-1/Input and Output Files by Case/E3 and Company Defined Cases/Market DGPV (Reference)/OA_NOLNG/planned_installed_capacities.tab
Note on C128: from data/HECO Plans/PSIP-WebDAV/2017-01-31 Response to Parties IRs/CA-IR-1/Input and Output Files by Case/E3 and Company Defined Cases/Market DGPV (Reference)/OA_NOLNG/planned_installed_capacities.tab
Note on A191: 444 MW DistPV installed by 2016 according to PSIP 2016-04-01 Figure J-19

## HECO non-plant O&M
2018 production from HECO-owned plants (from EIA form 923)
Plant Id | Combined Heat And Power Plant | Nuclear Unit Id | Plant Name | Operator Name | Operator Id | Plant State | Census Region | NERC Region | Reserved | NAICS Code | EIA Sector Number | Sector Name | Reported Prime Mover | Reported Fuel Type Code | AER Fuel Type Code | Reserved | Reserved | Physical Unit Label | Quantity January | Quantity February | Quantity March | Quantity April | Quantity May | Quantity June | Quantity July | Quantity August | Quantity September | Quantity October | Quantity November | Quantity December | Elec_Quantity January | Elec_Quantity February | Elec_Quantity March | Elec_Quantity April | Elec_Quantity May | Elec_Quantity June | Elec_Quantity July | Elec_Quantity August | Elec_Quantity September | Elec_Quantity October | Elec_Quantity November | Elec_Quantity December | MMBtuPer_Unit January | MMBtuPer_Unit February | MMBtuPer_Unit March | MMBtuPer_Unit April | MMBtuPer_Unit May | MMBtuPer_Unit June | MMBtuPer_Unit July | MMBtuPer_Unit August | MMBtuPer_Unit September | MMBtuPer_Unit October | MMBtuPer_Unit November | MMBtuPer_Unit December | Tot_MMBtu January | Tot_MMBtu February | Tot_MMBtu March | Tot_MMBtu April | Tot_MMBtu May | Tot_MMBtu June | Tot_MMBtu July | Tot_MMBtu August | Tot_MMBtu September | Tot_MMBtu October | Tot_MMBtu November | Tot_MMBtu December | Elec_MMBtu January | Elec_MMBtu February | Elec_MMBtu March | Elec_MMBtu April | Elec_MMBtu May | Elec_MMBtu June | Elec_MMBtu July | Elec_MMBtu August | Elec_MMBtu September | Elec_MMBtu October | Elec_MMBtu November | Elec_MMBtu December | Netgen January | Netgen February | Netgen March | Netgen April | Netgen May | Netgen June | Netgen July | Netgen August | Netgen September | Netgen October | Netgen November | Netgen December | Total Fuel Consumption Quantity | Electric Fuel Consumption Quantity | Total Fuel Consumption MMBtu | Elec Fuel Consumption MMBtu | Net Generation (Megawatthours) | YEAR
765 | N | . | Kahe | Hawaiian Electric Co Inc | 19547 | HI | PACN | HICC |  | 22 | 1 | Electric Utility | ST | DFO | DFO |  |  | barrels | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2018
765 | N | . | Kahe | Hawaiian Electric Co Inc | 19547 | HI | PACN | HICC |  | 22 | 1 | Electric Utility | ST | PG | WOO |  |  | mcf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2018
765 | N | . | Kahe | Hawaiian Electric Co Inc | 19547 | HI | PACN | HICC |  | 22 | 1 | Electric Utility | ST | RFO | RFO |  |  | barrels | 334829 | 318654 | 291176 | 328339 | 384634 | 360017 | 368762 | 373610 | 368950 | 383533 | 318772 | 299366 | 334829 | 318654 | 291176 | 328339 | 384634 | 360017 | 368762 | 373610 | 368950 | 383533 | 318772 | 299366 | 6.318 | 6.285 | 6.333 | 6.325 | 6.32 | 6.327 | 6.314 | 6.327 | 6.33 | 6.305 | 6.323 | 6.311 | 2115450 | 2002740 | 1844018 | 2076744 | 2430887 | 2277828 | 2328363 | 2363830 | 2335454 | 2418176 | 2015595 | 1889299 | 2115450 | 2002740 | 1844018 | 2076744 | 2430887 | 2277828 | 2328363 | 2363830 | 2335454 | 2418176 | 2015595 | 1889299 | 200295 | 190460 | 172811 | 191971 | 229500 | 212707 | 217755 | 220740 | 218968 | 224506 | 193297 | 173459 | 4130642 | 4130642 | 26098384 | 26098384 | 2446469 | 2018
766 | N | . | Waiau | Hawaiian Electric Co Inc | 19547 | HI | PACN | HICC |  | 22 | 1 | Electric Utility | GT | DFO | DFO |  |  | barrels | 8282 | 13347 | 6303 | 11270 | 4034 | 5635 | 4672 | 9579 | 10960 | 12401 | 4362 | 1267 | 8282 | 13347 | 6303 | 11270 | 4034 | 5635 | 4672 | 9579 | 10960 | 12401 | 4362 | 1267 | 5.726 | 5.719 | 5.718 | 5.717 | 5.729 | 5.759 | 5.759 | 5.722 | 5.716 | 5.72 | 5.735 | 5.735 | 47423 | 76331 | 36041 | 64431 | 23111 | 32452 | 26906 | 54811 | 62647 | 70934 | 25016 | 7266 | 47423 | 76331 | 36041 | 64431 | 23111 | 32452 | 26906 | 54811 | 62647 | 70934 | 25016 | 7266 | 1656 | 2930 | 1083 | 2297 | 804 | 835 | 980 | 2062 | 3072 | 3486 | 1283 | 278 | 92112 | 92112 | 527369 | 527369 | 20766 | 2018
766 | N | . | Waiau | Hawaiian Electric Co Inc | 19547 | HI | PACN | HICC |  | 22 | 1 | Electric Utility | ST | DFO | DFO |  |  | barrels | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2018
766 | N | . | Waiau | Hawaiian Electric Co Inc | 19547 | HI | PACN | HICC |  | 22 | 1 | Electric Utility | ST | PG | WOO |  |  | mcf | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2018
766 | N | . | Waiau | Hawaiian Electric Co Inc | 19547 | HI | PACN | HICC |  | 22 | 1 | Electric Utility | ST | RFO | RFO |  |  | barrels | 153975 | 154583 | 120960 | 123828 | 141214 | 104710 | 134373 | 130340 | 161168 | 165183 | 156740 | 136208 | 153975 | 154583 | 120960 | 123828 | 141214 | 104710 | 134373 | 130340 | 161168 | 165183 | 156740 | 136208 | 6.181 | 6.291 | 6.313 | 6.342 | 6.278 | 6.324 | 6.323 | 6.316 | 6.305 | 6.305 | 6.322 | 6.309 | 951719 | 972482 | 763620 | 785317 | 886541 | 662186 | 849640 | 823227 | 1016164 | 1041479 | 990910 | 859336 | 951719 | 972482 | 763620 | 785317 | 886541 | 662186 | 849640 | 823227 | 1016164 | 1041479 | 990910 | 859336 | 86289 | 88699 | 70611 | 70776 | 82573 | 59367 | 75721 | 71954 | 92528 | 95878 | 90833 | 77900 | 1683282 | 1683282 | 10602621 | 10602621 | 963129 | 2018
8823 | N | . | Barber's Point Tank Farm | Hawaiian Electric Co Inc | 19547 | HI | PACN |  |  | 22 | 1 | Electric Utility | ST | DFO | DFO |  |  | barrels | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2018
8823 | N | . | Barber's Point Tank Farm | Hawaiian Electric Co Inc | 19547 | HI | PACN |  |  | 22 | 1 | Electric Utility | ST | RFO | RFO |  |  | barrels | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2018
56329 | N | . | Campbell Industrial Park | Hawaiian Electric Co Inc | 19547 | HI | PACN | HICC |  | 22 | 1 | Electric Utility | GT | DFO | DFO |  |  | barrels | 0 | 0 | 0 | 1374 | 0 | 0 | 0 | 0 | 0 | 0 | 22711 | 13223 | 0 | 0 | 0 | 1374 | 0 | 0 | 0 | 0 | 0 | 0 | 22711 | 13223 | 0 | 0 | 0 | 5.71 | 0 | 0 | 0 | 0 | 0 | 0 | 5.731 | 5.728 | 0 | 0 | 0 | 7846 | 0 | 0 | 0 | 0 | 0 | 0 | 130157 | 75741 | 0 | 0 | 0 | 7846 | 0 | 0 | 0 | 0 | 0 | 0 | 130157 | 75741 | 0 | 0 | 0 | 500.669 | 0 | 0 | 0 | 0 | 0 | 0 | 8084 | 4162 | 37308 | 37308 | 213744 | 213744 | 12746.669 | 2018
56329 | N | . | Campbell Industrial Park | Hawaiian Electric Co Inc | 19547 | HI | PACN | HICC |  | 22 | 1 | Electric Utility | GT | OBL | ORW |  |  | barrels | 23567 | 10867 | 6860 | 17779 | 3481 | 0 | 0 | 0 | 0 | 6894 | 0 | 0 | 23567 | 10867 | 6860 | 17779 | 3481 | 0 | 0 | 0 | 0 | 6894 | 0 | 0 | 5.321 | 5.325 | 5.299 | 5.293 | 5.253 | 0 | 0 | 0 | 0 | 5.725 | 0 | 0 | 125400 | 57867 | 36351 | 94104 | 18286 | 0 | 0 | 0 | 0 | 39468 | 0 | 0 | 125400 | 57867 | 36351 | 94104 | 18286 | 0 | 0 | 0 | 0 | 39468 | 0 | 0 | 7726 | 3420 | 1992 | 6005.331 | 857 | -190 | -104 | -344 | -333 | 2431 | 0 | 0 | 69448 | 69448 | 371476 | 371476 | 21460.331 | 2018
58469 | N | . | HNL Emergency Power Facility | Hawaiian Electric Co Inc | 19547 | HI | PACN | HICC |  | 22 | 1 | Electric Utility | IC | DFO | DFO |  |  | barrels | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2018
58469 | N | . | HNL Emergency Power Facility | Hawaiian Electric Co Inc | 19547 | HI | PACN | HICC |  | 22 | 1 | Electric Utility | IC | OBL | ORW |  |  | barrels | 92 | 87 | 93 | 87 | 88 | 89 | 92 | 92 | 83 | 91 | 90 | 94 | 92 | 87 | 93 | 87 | 88 | 89 | 92 | 92 | 83 | 91 | 90 | 94 | 5.271 | 5.271 | 5.271 | 5.271 | 5.271 | 5.271 | 5.271 | 5.271 | 5.271 | 5.271 | 5.271 | 5.271 | 485 | 459 | 490 | 459 | 464 | 469 | 485 | 485 | 437 | 480 | 474 | 495 | 485 | 459 | 490 | 459 | 464 | 469 | 485 | 485 | 437 | 480 | 474 | 495 | 51.526 | 48.498 | 52.343 | 48.904 | 49.2 | 49.832 | 51.276 | 51.483 | 46.558 | 50.911 | 50.567 | 52.902 | 1078 | 1078 | 5682 | 5682 | 604 | 2018
60328 | N | . | Schofield Generating Station | Hawaiian Electric Co Inc | 19547 | HI | PACN |  |  | 22 | 1 | Electric Utility | IC | DFO | DFO |  |  | barrels | . | . | . | . | . | 0 | 0 | 0 | 0 | 0 | 0 | 0 | . | . | . | . | . | 0 | 0 | 0 | 0 | 0 | 0 | 0 | . | . | . | . | . | 0 | 0 | 0 | 0 | 0 | 0 | 0 | . | . | . | . | . | 0 | 0 | 0 | 0 | 0 | 0 | 0 | . | . | . | . | . | 0 | 0 | 0 | 0 | 0 | 0 | 0 | . | . | . | . | . | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2018
60328 | N | . | Schofield Generating Station | Hawaiian Electric Co Inc | 19547 | HI | PACN |  |  | 22 | 1 | Electric Utility | IC | OBL | ORW |  |  | barrels | . | . | . | . | . | 3933 | 9243 | 8020 | 7797 | 8020 | 8494 | 6064 | . | . | . | . | . | 3933 | 9243 | 8020 | 7797 | 8020 | 8494 | 6064 | . | . | . | . | . | 5.293 | 5.268 | 5.271 | 5.264 | 5.29 | 5.282 | 5.285 | . | . | . | . | . | 20817 | 48692 | 42273 | 41043 | 42426 | 44865 | 32048 | . | . | . | . | . | 20817 | 48692 | 42273 | 41043 | 42426 | 44865 | 32048 | . | . | . | . | . | 2171 | 5647 | 4830 | 4750 | 4921 | 5221 | 3691 | 51571 | 51571 | 272164 | 272164 | 31231 | 2018
61851 | N | . | Campbell Industrial Park BESS | Hawaiian Electric Co Inc | 19547 | HI | PACN |  |  | 22 | 1 | Electric Utility | BA | MWH | OTH |  |  |  | 27 | 25 | 28 | 26 | 27 | 29 | 29 | 29 | 25 | 28 | 28 | 29 | 27 | 25 | 28 | 26 | 27 | 29 | 29 | 29 | 25 | 28 | 28 | 29 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -16.075 | -14.529 | -16.383 | -15.248 | -15.816 | -16.652 | -16.697 | -16.878 | -14.833 | -16.051 | -16.049 | -16.789 | 330 | 330 | 0 | 0 | -192 | 2018
prime mover | fixed O&M ($/kW-y) | variable O&M ($/MWh) | category | capacity online 2017 | MWh gen 2018 | 2018 O&M
ST | 9.8583 | 9.6723 | steam | 974.5 | 3409598 | 42585681.2929
GT | 17.4846 | 0.18601 | non-steam | 215.8 | 54973 | 3783399.0833
IC | 34.46 | 20.96 | non-steam | 161.84 | 31835 | 6244268
BA | 37.11 | 0 | non-steam | 1 | -192 | 37110
Generation O&M expenses | From 2018 FERC Form 1 "Electric Operation and Maintenance Expenses", hard to retrieve in digital form, but also available at https://puc.hawaii.gov/wp-content/uploads/2019/08/AFR-HECO-2018.pdf
steam power production | 56520163
non-steam power production | 15437622
O&M not attributable to individual plants | 19307326.6238
Note on B24: from new generator data workbook (PSIP 2016-12 ATB 2019 generator data.xlsx)
Note on C24: from new generator data workbook (PSIP 2016-12 ATB 2019 generator data.xlsx)
Note on B25: from new generator data workbook (PSIP 2016-12 ATB 2019 generator data.xlsx)
Note on C25: from new generator data workbook (PSIP 2016-12 ATB 2019 generator data.xlsx)